## Sheet1
Tag Number | P&ID Sheet Number | Size and Rating | Connection Type | Type | Body Material | Trim | Port | Location | Client Pipe Class | Manufacturer | Model | Pipe Schedule | Notes
V100 | Sheet 1 | [6 empty] | 20-12"-P-5030-100-3CS11P
V101 | Sheet 1 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-12"-P-5030-100-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
CV102 | Sheet 1 | [6 empty] | 20-12"-P-5030-100-3CS11P
V103 | Sheet 1 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5030-101-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V104 | Sheet 1 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | 20-16"-P-5030-101-3CS11P | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V105 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5030-101-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V106 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5030-101-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V107 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-16"-P-5030-101-3CS11P | N/A | AGCO | M1-VIS-4-AM | Not Applicable | Teflon packing, metal seat
V108 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V109 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V110 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V111 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-16"-P-5031-102-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V112 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V113 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-16"-P-5031-102-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V114 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V115 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-16"-P-5031-102-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V116 | Sheet 12 | [6 empty] | 20-C-5021 Compressor Second Stage
V117 | Sheet 12 | [6 empty] | Instrumentation / Tubing
V118 | Sheet 12 | [6 empty] | 20-C-5021 Compressor First Stage
V119 | Sheet 12 | [6 empty] | Instrumentation / Tubing
V120 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V121 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V122 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V123 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V124 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V125 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V126 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V127 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V128 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V129 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V130 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V131 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V132 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V133 | Sheet 3 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-V-5124 Bulk Oil Seperator | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V134 | Sheet 3 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-V-5124 Bulk Oil Seperator | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V135 | Sheet 3 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-V-5124 Bulk Oil Seperator | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V136 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-106-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V137 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V138 | Sheet 4 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V139 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V140 | Sheet 4 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V141 | Sheet 4 | 8"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GABARH2F | Bolted Bonnet, Gear Operated, API 600, OS&Y, Bevel Gear Operator, Flexible Graphite Packing, Flexible/Solid Wedge
V142 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V143 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V144 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V145 | Sheet 4 | 8"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GABARH2F | Bolted Bonnet, Gear Operated, API 600, OS&Y, Bevel Gear Operator, Flexible Graphite Packing, Flexible/Solid Wedge
V146 | Sheet 4 | [6 empty] | 20-8"-P-5033-107-3CS11P-HP
CV147 | Sheet 4 | 8"-300# | RF Flange | Swing Check | ASTM A216 WCB | Trim # 8 | N/A | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | CSBARH1 | Bolted Cover, API 594
V148 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V149 | Sheet 6 | 8"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-8"-P-5035-108-3CS11P-HP | 3CS11 |  |  | GABARH2F | Bolted Bonnet, Gear Operated, API 600, OS&Y, Bevel Gear Operator, Flexible Graphite Packing, Flexible/Solid Wedge
V150 | Sheet 6 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5035-108-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V151 | Sheet 6 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5035-108-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V152 | Sheet 6 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V153 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V154 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V155 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V156 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V157 | Sheet 7 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-2"-P-5036-112-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V158 | Sheet 7 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-2"-P-5036-112-3CS11P-H-TE | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V159 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V160 | Sheet 7 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-2"-P-5036-112-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V161 | Sheet 7 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-2"-P-5036-113-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V162 | Sheet 7 | [6 empty] | 20-2"-P-5036-113-3CS11P
V163 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V164 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V165 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V166 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V167 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V168 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V169 | Sheet 9 | 6"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GABARH1F | Bolted Bonnet, API 600, OS&Y, Flexible Graphite Packing, Flexible/Solid Wedge
CV170 | Sheet 9 | 2"-300# | RF Flange | Swing Check | ASTM A216 WCB | Trim # 8 | N/A | 20-2"-P-5038-113-3CS11P | 3CS11 |  |  | CSBARH1 | Bolted Cover, API 594
V200 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V201 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | 20-6"-P-5038-200-3CS11P-H | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V202 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V203 | Sheet 9 | 1/2" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V204 | Sheet 9 | 1/2" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V205 | Sheet 9 | 1/2" | FNPT | 3-Valve Manifold - FT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V206 | Sheet 9 | [6 empty] | 20-6"-P-5038-200-3CS11P-H
V207 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5038-201-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V208 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V209 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5038-201-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V210 | Sheet 10 | 2"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-4"-P-5039-202-3CS11P-H | 3CS11 |  |  | GABARH1F | Bolted Bonnet, API 600, OS&Y, Flexible Graphite Packing, Flexible/Solid Wedge
V211 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-202-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V212 | Sheet 10 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V213 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-202-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V214 | Sheet 10 | [6 empty] | 20-4"-P-5039-202-3CS11P-H
V215 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V216 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V217 | Sheet 10 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V218 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V219 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V220 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V221 | Sheet 10 | [6 empty] | 20-4"-P-5039-203-3CS11P-H
V222 | Sheet 10 | [6 empty] | 20-4"-P-5039-203-3CS11P-H
V223 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V224 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V225 | Sheet 10 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat

## Input Sheet
Tag Number | P&ID Sheet Number | Size and Rating | Connection Type | Type | Body Material | Trim | Port | Location | Client Pipe Class | Manufacturer | Model | Pipe Schedule | Notes
V100 | Sheet 1 | [6 empty] | 20-12"-P-5030-100-3CS11P
V101 | Sheet 1 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-12"-P-5030-100-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
CV102 | Sheet 1 | [6 empty] | 20-12"-P-5030-100-3CS11P
V103 | Sheet 1 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5030-101-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V104 | Sheet 1 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | 20-16"-P-5030-101-3CS11P | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V105 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5030-101-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V106 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5030-101-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V107 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-16"-P-5030-101-3CS11P | N/A | AGCO | M1-VIS-4-AM | Not Applicable | Teflon packing, metal seat
V108 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V109 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V110 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V111 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-16"-P-5031-102-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V112 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V113 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-16"-P-5031-102-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V114 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-16"-P-5031-102-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V115 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-16"-P-5031-102-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V116 | Sheet 12 | [6 empty] | 20-C-5021 Compressor Second Stage
V117 | Sheet 12 | [6 empty] | Instrumentation / Tubing
V118 | Sheet 12 | [6 empty] | 20-C-5021 Compressor First Stage
V119 | Sheet 12 | [6 empty] | Instrumentation / Tubing
V120 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V121 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V122 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V123 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V124 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V125 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V126 | Sheet 2 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V127 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V128 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V129 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V130 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V131 | Sheet 2 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5031-104-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V132 | Sheet 2 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-8"-P-5031-104-3CS11P-HP | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V133 | Sheet 3 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-V-5124 Bulk Oil Seperator | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V134 | Sheet 3 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-V-5124 Bulk Oil Seperator | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V135 | Sheet 3 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | 20-V-5124 Bulk Oil Seperator | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V136 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-106-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V137 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V138 | Sheet 4 | 1/2" | FNPT | 3-Valve Manifold - PDT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V139 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V140 | Sheet 4 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V141 | Sheet 4 | 8"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GABARH2F | Bolted Bonnet, Gear Operated, API 600, OS&Y, Bevel Gear Operator, Flexible Graphite Packing, Flexible/Solid Wedge
V142 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V143 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V144 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V145 | Sheet 4 | 8"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GABARH2F | Bolted Bonnet, Gear Operated, API 600, OS&Y, Bevel Gear Operator, Flexible Graphite Packing, Flexible/Solid Wedge
V146 | Sheet 4 | [6 empty] | 20-8"-P-5033-107-3CS11P-HP
CV147 | Sheet 4 | 8"-300# | RF Flange | Swing Check | ASTM A216 WCB | Trim # 8 | N/A | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | CSBARH1 | Bolted Cover, API 594
V148 | Sheet 4 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5033-107-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V149 | Sheet 6 | 8"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-8"-P-5035-108-3CS11P-HP | 3CS11 |  |  | GABARH2F | Bolted Bonnet, Gear Operated, API 600, OS&Y, Bevel Gear Operator, Flexible Graphite Packing, Flexible/Solid Wedge
V150 | Sheet 6 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5035-108-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V151 | Sheet 6 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-8"-P-5035-108-3CS11P-HP | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V152 | Sheet 6 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V153 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V154 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V155 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V156 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V157 | Sheet 7 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-2"-P-5036-112-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V158 | Sheet 7 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | 20-2"-P-5036-112-3CS11P-H-TE | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V159 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V160 | Sheet 7 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-2"-P-5036-112-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V161 | Sheet 7 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-2"-P-5036-113-3CS11P | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V162 | Sheet 7 | [6 empty] | 20-2"-P-5036-113-3CS11P
V163 | Sheet 7 | [6 empty] | 20-2"-P-5036-112-3CS11P-H-TE
V164 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V165 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V166 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V167 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V168 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V169 | Sheet 9 | 6"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-6"-P-5038-114-3CS11P-H-TE | 3CS11 |  |  | GABARH1F | Bolted Bonnet, API 600, OS&Y, Flexible Graphite Packing, Flexible/Solid Wedge
CV170 | Sheet 9 | 2"-300# | RF Flange | Swing Check | ASTM A216 WCB | Trim # 8 | N/A | 20-2"-P-5038-113-3CS11P | 3CS11 |  |  | CSBARH1 | Bolted Cover, API 594
V200 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V201 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | 20-6"-P-5038-200-3CS11P-H | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V202 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V203 | Sheet 9 | 1/2" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V204 | Sheet 9 | 1/2" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-6"-P-5038-200-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V205 | Sheet 9 | 1/2" | FNPT | 3-Valve Manifold - FT | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | Rosemount |  | Not Applicable | Teflon packing, metal seat
V206 | Sheet 9 | [6 empty] | 20-6"-P-5038-200-3CS11P-H
V207 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5038-201-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V208 | Sheet 9 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V209 | Sheet 9 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5038-201-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V210 | Sheet 10 | 2"-300# | RF Flange | Gate | ASTM A216 WCB | Trim # 8 | Full Port | 20-4"-P-5039-202-3CS11P-H | 3CS11 |  |  | GABARH1F | Bolted Bonnet, API 600, OS&Y, Flexible Graphite Packing, Flexible/Solid Wedge
V211 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-202-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V212 | Sheet 10 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V213 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-202-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V214 | Sheet 10 | [6 empty] | 20-4"-P-5039-202-3CS11P-H
V215 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V216 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V217 | Sheet 10 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat
V218 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V219 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V220 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V221 | Sheet 10 | [6 empty] | 20-4"-P-5039-203-3CS11P-H
V222 | Sheet 10 | [6 empty] | 20-4"-P-5039-203-3CS11P-H
V223 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V224 | Sheet 10 | 3/4" Class 800 | SW x NPT | Gate | ASTM A105N | Trim # 8 | Conventional | 20-4"-P-5039-203-3CS11P-H | 3CS11 |  |  | GASACH1F | Bolted Bonnet, API 602, OS&Y, Flexible Graphite Packing, Solid Wedge, Certified Low Emissions
V225 | Sheet 10 | 1/2" | FNPT | 2-Valve Manifold - PG | Stainless Steel | N/A | N/A | Instrumentation / Tubing | N/A | AGCO | PTM-VIS-4 with V6-VIS-4 | Not Applicable | Teflon packing, metal seat